## Capacities
Transmission Line Capacities
Capacity
| (MW) | Comments
765 kV AC Single Circuit | 3000 | CPC
500 kV AC Single Circuit | 1500 | Frontier Line Analysis, 12/06 (FL), Canada/PNW - Northern California Transmission Report, 11/07 (CPC)
500 kV AC Double Circuit | 3000 | 2x single circuit
345 kV AC Single Circuit | 750 | Sub-group consensus
345 kV AC Double Circuit | 1500 | 2x single circuit
230 kV AC Single Circuit | 400 | Sub-group consensus
230 kV AC Double Circuit | 800 | 2x single circuit
500 kV DC Bi-Pole | 3000 | FL, CPC
800 kV DC Bi-Pole | TBD
Note: Capacity of first higher voltage line added in an area will be discounted to reflect capacity of existing lower voltage lines.
For example, first 500 kV line in area with existing 345 kV lines will have 750 MW capacity.

## Lines
Transmission Line Capital Costs
Cap Cost
| $000/mile | Mult. | Comments
765 kV AC Single Circuit | 2250 | 1.25 | Sub-group consensus
500 kV AC Single Circuit | 1800 | 1 | Frontier Line Analysis, 12/06 (FL), Canada/PNW - Northern California Transmission Report, 11/07 (CPC)*
500 kV AC Double Circuit | 2880 | 1.6 | 1.6x single circuit, FL, CPC
345 kV AC Single Circuit | 1260 | 0.7 | Sub-group consensus
345 kV AC Double Circuit | 2016 | 1.12 | 1.6x single circuit
230 kV AC Single Circuit | 900 | 0.5 | Sub-group consensus
230 kV AC Double Circuit | 1440 | 0.8 | 1.6x single circuit
500 kV DC Bi-Pole | 1440 | 0.8 | 0.8x 500 kV AC, FL, CPC
800 kV DC Bi-Pole | TBD
* FL & CPC used $2 million per mile with $300k for ROW (outside California). Sub-group consensus is to use $2 million per mile, but our ROW costs (outside CA) are about $200k.
Costs include all capital costs (construction, permitting, AFUDC, etc) except ROW
*

## ROW
ROW Costs
ROW Width
| feet | Comments
765 kV AC Single Circuit | 200
500 kV AC Single Circuit | 175
500 kV AC Double Circuit | 175 | same as single circuit
345 kV AC Single Circuit | 160
345 kV AC Double Circuit | 160 | same as single circuit
230 kV AC Single Circuit | 150
230 kV AC Double Circuit | 150 | same as single circuit
500 kV DC Bi-Pole | 200
800 kV DC Bi-Pole | TBD
Note: Single circuit ROW widths from Rich Bayless research.
State/Provincial Multipliers
| Mult | $/acre | $000/mile
| /1 | /2 | 200' ROW
Alberta | 0.34 | 9350 | 226.6667
Arizona | 0.345 | 9487.5 | 230
British Columbia | 0.34 | 9350 | 226.6667
California | 1 | 27500 | 666.6667
CFE | 0.068 | 1870 | 45.3333
Colorado | 0.307 | 8442.5 | 204.6667
Idaho | 0.341 | 9377.5 | 227.3333
Montana | 0.224 | 6160 | 149.3333
Nevada | 0.39 | 10725 | 260
New Mexico | 0.17 | 4675 | 113.3333
Oregon | 0.341 | 9377.5 | 227.3333
Washington | 0.341 | 9377.5 | 227.3333
Utah | 0.357 | 9817.5 | 238
Wyoming | 0.188 | 5170 | 125.3333
/1 - Multipliers from E3 spreadsheet
/2 - California $/acre from E3 spreadsheet
Zone Multipliers
| Mult | $/acre | $000/mile
| /1 | /2 | 200' ROW
California | 1 | 27500 | 666.6667
CFE | 0.068 | 1870 | 45.3333
Inland Rural (MT, NM, WY) | 0.194 | 5335 | 129.3333
All Other | 0.34467 | 9478.3333 | 229.7778

## Subs
Substation Costs
Cap Cost
| $000 | Comments
500 kV - no tx | 50000 | IPC Planning Assumptions
500 kV - 1500 MVA tx | 100000 | IPC Planning Assumptions
345 kV - no tx | 40000 | IPC Planning Assumptions
345 kV - 1000 MVA tx | 75000 | IPC Planning Assumptions
230 kV - no tx | 35000 | IPC Planning Assumptions
230 kV - 500 MVA tx | 50000 | IPC Planning Assumptions
765 kV - no tx | 62500 | 1.25x 500 kV, Sub-group consensus
765 kV - w/ tx | 125000 | 1.25x 500 kV, Sub-group consensus
500 kV DC terminal, 3000 MW | 250000 | FL, CPC
800 kV DC terminal, | TBD
AC substations include reactive support and series comp
Typical Distance between AC Substations
miles
765 kV | 300
500 kV | 200
345 kV | 150
230 kV | 100

## O&M
Transmission Line O&M Costs
(% of Capital Costs)
| Oper & | Tax &
Source | Maint | Insurance | Total
PacifiCorp | 2.25% | 0.5% | 2.75% | insurance included in O&M
PG&E | 1% | 2.5% | 3.5%
Trans-Elect | 1.3% | 1.5% | 2.8%
Average | 1.517% | 1.5% | 3.017%
| Oper & | Tax &
Source | Maint | Insurance | Total
PacifiCorp | 1.25% | 1.5% | 2.75% | 1% for insurance shifted out of O&M
PG&E | 1% | 2.5% | 3.5%
Trans-Elect | 1.3% | 1.5% | 2.8%
Average | 1.183% | 1.833% | 3.017%
Rounded | 1.2% | 1.8% | 3%

## Losses
Transmission Line Losses
50°C
|  | Phase/Pole |  | No. of | Resistance
| Capacity | Current | Typical | Conductors | Per Cond | FLL* | FLL* per
| (MW) | (amps) | Conductors | per phase | (ohms/mile) | (MW/mile) | 100 miles | Comments
765 kV AC Single | 3000 | 2383.2828 | 957 ACSR | 6 | 0.1086 | 0.30843 | 1.028% | AEP
500 kV AC Single | 1500 | 1823.2114 | 1590 ACSR | 3 | 0.0666 | 0.22139 | 1.476% | Black & Veatch
500 kV AC Double | 3000 | 1823.2114 | 1590 ACSR | 3 | 0.0666 | 0.44277 | 1.476% | Black & Veatch
345 kV AC Single | 750 | 1321.1677 | 795 ACSR | 2 | 0.128 | 0.33513 | 4.468% | Black & Veatch
345 kV AC Double | 1500 | 1321.1677 | 795 ACSR | 2 | 0.128 | 0.67027 | 4.468% | Black & Veatch
230 kV AC Single | 400 | 1056.9341 | 1272 ACSR | 1 | 0.0828 | 0.27749 | 6.937% | Black & Veatch
230 kV AC Double | 800 | 1056.9341 | 1272 ACSR | 1 | 0.0828 | 0.55498 | 6.937% | Black & Veatch
500 kV DC Bi-Pole | 3000 | 3000 | 1780 ACSR | 3 | 0.0609 | 0.3654 | 1.218% | Black & Veatch
800 kV DC Bi-Pole | 4500 | 2812.5 | 1780 ACSR | 3 | 0.0609 | 0.32115 | 0.7137% | Black & Veatch
*FLL = Full Load Losses for all circuits
AC Power Factor: | 0.95
DC Terminal losses: | 1.5%
Note: Conductor bundles for 345 kV and 230 kV are reasonable for local projects. However, bigger bundles may be more appropriate to
reduce losses for long distance projects.
Methodology for adjusting FLL for capacity factor
Example for 50% capacity factor:
Maximum Possible, 50% of hours at full load = 0.5 * FLL
Minimum Possible, all hours at 50% of full load = 0.5^2 * FLL = 0.25 * FLL
Average = ((0.5 * FLL) + (0.25 * FLL)/2 = 0.375 * FLL
| CF | Max | Min | Avg
|  | *FLL | *FLL | *FLL
| 20% | 0.2 | 0.04 | 0.12
| 40% | 0.4 | 0.16 | 0.28
| 60% | 0.6 | 0.36 | 0.48
| 80% | 0.8 | 0.64 | 0.72